## Slide 1: WIRELESS HART
PREPARED BY,
S.BABITHA,AP,
IT,HITS.

## Slide 2: DEFN
WirelessHART (Wireless Highway Addressable Remote Transducer Protocol) is a wireless communication protocol specifically designed for industrial CPS applications, especially in process automation and control systems.
It extends the wired HART protocol by adding wireless capabilities while maintaining compatibility with existing HART devices.

## Slide 3: 🔑 Key Features of WirelessHART
Feature | Description
Based on IEEE 802.15.4 | Operates in the 2.4 GHz ISM band, using 802.15.4 physical layer (same as Zigbee).
Mesh Networking | Supports self-organizing and self-healing mesh topology for high reliability.
Time-Synchronized | Uses TDMA (Time Division Multiple Access) to schedule communications and avoid collisions.
Secure | End-to-end encryption, authentication, and message integrity using AES-128.
Backwards-Compatible | Works with legacy HART devices via gateways.
Deterministic Communication | Supports real-time data transmission with bounded latency.

## Slide 4: Typical Architecture of a WirelessHART Network
[Field Devices] ↔ [Routers/Repeater Nodes] ↔ [WirelessHART Gateway] ↔ [Host System / Controller]
Field Devices: Wireless sensors/actuators (temperature, pressure, flow meters)
Routers: Relay data to extend range and improve reliability
Gateway: Converts WirelessHART to standard protocols (Modbus, Ethernet, etc.)
Host System: SCADA, DCS, or cloud controller

## Slide 5: Applications in CPS
Application Area | Examples
Process Automation | Oil refineries, chemical plants, gas pipelines
Industrial Monitoring | Pressure, flow, temperature sensing in hazardous or hard-to-reach areas
Smart Manufacturing | Asset tracking, machine health diagnostics
Environmental Monitoring | Air quality and emissions data collection

## Slide 6: Advantages of WirelessHART in CPS
No need for extensive cabling – reduces cost and complexity
High reliability in noisy industrial environments
Supports both monitoring and control
Energy-efficient design for battery-operated devices
Scalable and easily expandable network

## Slide 7: Limitations
Limited bandwidth (suitable for low-data-rate applications)
Operates in the crowded 2.4 GHz band (possible interference)
Latency not suitable for ultra-time-critical systems